## Load List
Load ID | Load Name | Type | Power (kW) | Voltage (V) | Phases | Power Factor | Efficiency | Current (A) | Design Current (A) | Cable Size (mm²) | Breaker Rating (A) | Voltage Drop (%) | Source Bus | Priority
L001 | CNC Milling Machine 1 | motor | 15 | 400 | 3 | 0.85 | 0.9 | 28.3 | 35.38 | 10 | 40 | 0.73 | B002 | essential
L002 | CNC Milling Machine 2 | motor | 12 | 400 | 3 | 0.85 | 0.9 | 22.64 | 28.3 | 6 | 32 | 1.16 | B002 | essential
L003 | CNC Lathe | motor | 18 | 400 | 3 | 0.85 | 0.9 | 33.96 | 42.45 | 10 | 50 | 0.7 | B002 | essential
L004 | Main Conveyor Belt Motor | motor | 7.5 | 400 | 3 | 0.85 | 0.9 | 14.15 | 17.69 | 2.5 | 20 | 2.59 | B002 | essential
L005 | Secondary Conveyor Motors | motor | 5.5 | 400 | 3 | 0.85 | 0.9 | 10.38 | 12.98 | 2.5 | 16 | 1.48 | B002 | essential
L006 | Welding Robot Power Supply | general | 25 | 400 | 3 | 0.9 | 0.9 | 44.55 | 44.55 | 16 | 50 | 0.37 | B002 | essential
L007 | Production HVAC System | hvac | 45 | 400 | 3 | 0.85 | 0.9 | 84.9 | 106.12 | 70 | 125 | 0.7 | B002 | essential
L008 | Dust Collection System | motor | 22 | 400 | 3 | 0.85 | 0.9 | 41.51 | 51.89 | 16 | 63 | 1.08 | B002 | essential
L009 | Office Lighting Circuit 1 | lighting | 8.5 | 230 | 1 | 0.85 | 0.9 | 48.31 | 60.39 | 25 | 63 | 1.42 | B003 | non-essential
L010 | Office Lighting Circuit 2 | lighting | 6.2 | 230 | 1 | 0.85 | 0.9 | 35.24 | 44.05 | 16 | 50 | 1.46 | B003 | non-essential
L011 | Office Computers & Equipment | general | 12 | 230 | 1 | 0.95 | 0.9 | 61.02 | 76.28 | 35 | 80 | 1.06 | B003 | non-essential
L012 | Kitchen Appliances | general | 15 | 400 | 3 | 0.85 | 0.9 | 28.3 | 28.3 | 10 | 32 | 0.7 | B003 | non-essential
L013 | Office HVAC System | hvac | 28 | 400 | 3 | 0.85 | 0.9 | 52.83 | 66.04 | 25 | 80 | 0.79 | B003 | essential
L014 | Emergency Lighting | lighting | 5 | 230 | 1 | 0.85 | 0.9 | 28.42 | 35.53 | 10 | 40 | 2.71 | B001 | critical
L015 | Critical Systems UPS | ups | 20 | 400 | 3 | 0.9 | 0.9 | 35.64 | 44.55 | 16 | 50 | 0.61 | B001 | critical
L016 | Process Water Pumps | motor | 11 | 400 | 3 | 0.85 | 0.9 | 20.75 | 25.94 | 6 | 32 | 2.3 | B001 | essential
L017 | Air Compressor | motor | 30 | 400 | 3 | 0.85 | 0.9 | 56.6 | 70.75 | 35 | 80 | 0.7 | B001 | essential
L018 | Workshop Equipment | general | 8 | 400 | 3 | 0.85 | 0.9 | 15.09 | 15.09 | 2.5 | 16 | 3.44 | B001 | non-essential